TRIBHUVAN UNIVERSITY

INSTITUTE OF ENGINEERING

PULCHOWK CAMPUS

THESIS NO: M-154-MSESPM-2018-2022

Optimal Transmission Expansion Planning of Bagmati Province of Nepal Using Mixed-Integer Linear Programming

by

Rabi Sapkota

A THESIS

SUBMITTED TO THE DEPARTMENT OF MECHANICAL AND AEROSPACE ENGINEERING IN PARTIAL FULFILMENT OF THE REQUIREMENTS FOR THE DEGREE OF MASTER OF SCIENCE IN ENERGY SYSTEM PLANNING AND MANAGEMENT

DEPARTMENT OF MECHANICAL AND AEROSPACE ENGINEERING

LALITPUR, NEPAL

SEPTEMBER, 2022

- COPYRIGHT

The author has agreed that the library, Department of Mechanical and Aerospace Engineering Pulchowk Campus, Institute of Engineering may make this thesis freely available for inspection. Moreover, the author has agreed that permission for extensive copying of this thesis for scholarly purpose may be granted by the professor(s) who supervised the work recorded herein or, in their absence, by the Head of the Department wherein the thesis was done. It is understood that the recognition will be given to the authorof this thesis and to the Department of Mechanical Engineering, Pulchowk Campus, Institute of Engineering in any use of the material of this thesis. Copying or publication or the other use of this thesis for financial gain without approval of the Department of Mechanical and Aerospace Engineering, Pulchowk Campus, Institute of Engineering and author’s written permission is prohibited. Request for permission to copy or to make any other use of the material in this thesis in whole or in part should be addressed to:

Head

Department of Mechanical and Aerospace Engineering

Pulchowk Campus, Institute of Engineering

Lalitpur, Nepal

TRIBHUVAN UNIVERSITY

INSTITUTE OF ENGINEERING

PULCHOWK CAMPUS

DEPARTMENT OF MECHANICAL AND AEROSPACE ENGINEERING

The undersigned certify that they have read, and recommended to the Institute of Engineering for acceptance, a thesis entitled "Optimal Transmission Expansion Planning of Bagmati Province of Nepal Using Mixed-Integer Linear Programming” submitted by Mr. Rabi Sapkota in partial fulfillment of the requirements for the degree of Master of Science in Energy System Planning and Management.

Supervisor, Dr. Sanjeev Maharjan, Assistant Professor

Department of Mechanical and Aerospace Engineering, Pulchowk Campus

Co- Supervisor, Er. Shahabuddin Khan, Assistant Professor

Department of Electrical Engineering, Pulchowk Campus

External Examiner, Er. Birendra Kumar Jha, Manager

Nepal Electricity Authority

Committee Chairperson, Dr. Surya Prasad Adhikari, Associate Professor & Head of Department

Department of Mechanical and Aerospace Engineering, Pulchowk Campus

Date: 20th September 2022

- ABSTRACT

For any country, proper planning of the transmission system is important for creating a secure and reliable transmission grid. Government of Nepal has set out various targets in the power generation sector keeping abundantly available hydro resources of the country in view, along with the development of other renewable energy sources. For the evacuation of energy generated from these resources, development of a strong and reliable transmission system is crucial and the development of the strong and reliable transmission system is only possible by proper and rational planning of the transmission system.

In this thesis, an optimization model based on a mixed integer static linear programming method is proposed for the high voltage transmission network expansion planning of Bagmati Province of Nepal considering the generation-load growth scenario for the year 2040. The objective function of the model is defined to find the minimum cost option for the high voltage transmission line expansion planning of the region.

This thesis can be divided into two parts. First, the existing transmission system of Bagmati province of Nepal is evaluated for the adequateness of the existing electrical transmission network for the generation-demand scenario for the year 2040. Then mixed-integer linear programming (MILP) based optimization model is formulated to determine the minimum-cost, high voltage transmission expansion plan for Bagmati Province of Nepal.

The static load flow analysis performed taking the existing network result shows that the existing transmission network of Bagmati province is not adequate for the generation load scenario for the year 2040. Out of 32 major transmission lines of voltage levels ranging from 66 kV to 400 kV, 14 lines are overloaded beyond their maximum thermal power transfer capacity.

The expansion solution provided by the planning model shows that the Lapsephedi-Bhaktapur, Lamosangu-Bhaktapur, Balaju-Chapali, Chapali-Mulpani, Mulpani-Bhaktapur lines should be expanded with additional 220 kV Double circuit lines having “Twin Bison” ACSR Conductors. Also, the Suichatar-Patan line segment is further expanded by adding a 66 kV single Circuit line with “Wolf” ACSR conductor. The total expansion cost is determined to be 72.409 Million USD.

- ACKNOWLEDGEMENT

First of all, I would like to express my deepest gratitude to my supervisors, Dr. Sanjeev Maharjan, Assistant Professor, Department of Mechanical and Aerospace Engineering, and Er. Shahabuddin Khan, Assistant Professor, Department of Electrical Engineering for accepting my thesis proposal and providing valuable instructions, guidance and insightful feedback on my work.

I would like to thank Dr. Nawaraj Bhattarai, Associate professor and Program Coordinator of the M.Sc. Energy System Planning Management, Dr. Surya Prasad Adhikari, Associate Professor & Head of Department of Mechanical and Aerospace Engineering and former Program coordinator of M.Sc. Energy System Planning Management, Dr. Shree Raj Shakya for their kind support. I also extend my gratitude to the entire faculty members of the Department of Mechanical and Aerospace Engineering, Institute of Engineering, Pulchowk Campus for providing necessary help during the study period.

I would also like to express my sincere thanks to Er. Birendra Kumar Jha, the external examiner of my thesis, for his constructive criticism and suggestions.

I am also thankful to all the colleagues of the MSc.-Energy System Planning Management 2074-batch, especially to Er. Kishor Ghimire, Er. Sumesh Raut, and Er. William Shrestha for their kind help and cooperation.

Finally, no amount of words will be enough to express gratitude to my parents for their love, support, inspiration, and encouragement.

# TABLE OF CONTENTS

COPYRIGHT	2

ABSTRACT	4

ACKNOWLEDGEMENT	5

TABLE OF CONTENTS	6

LIST OF FIGURES	8

LIST OF TABLES	9

LIST OF ACRONYMS AND ABBREVIATIONS	10

CHAPTER 1:	INTRODUCTION	11

1.1	Background	11

1.2	Rationale and Problem Statement	12

1.3	Objectives	13

1.3.1	Main Objective	13

1.3.2	Specific Objectives	13

1.4	Limitations	14

CHAPTER 2:	LITERATURE REVIEW	15

2.1	Background	15

2.2	Transmission Expansion Planning Approaches	15

2.2.1	TEP with Optimization Models	15

2.2.2	TEP with Heuristics Models	18

2.3	Based on Planning Horizon	18

2.4	Methods and Tools for Transmission System Planning	19

2.4.1	Consideration in Design of Transmission Line	19

2.4.2	Load Flow Methods	20

2.4.3	Mixed-integer Linear Programming	21

2.5	Literature insights and identified gaps	22

CHAPTER 3:	RESEARCH METHODOLOGY	24

3.1	Research Methodology	24

3.1.1	Issue Identification	25

3.1.2	Literature survey	25

3.1.3	Data collection	25

3.1.4	Load flow Analysis of Existing System	25

3.1.5	Method selection and Model development	27

3.1.6	Transmission Expansion Planning Model Formulation	27

3.1.7	Tools Selected	32

3.1.8	Model Writing and Model Testing	32

CHAPTER 4:	RESULTS AND DISCUSSION	33

4.1	Load Flow Analysis of Existing Transmission System	33

4.2	Garver’s 6 bus test system	36

4.3	Bagmati Province High Voltage Transmission Expansion Planning	39

CHAPTER 5:	CONCLUSIONS AND RECOMMENDATIONS	47

5.1	Conclusions	47

5.2	Recommendations	48

REFERENCES	49

APPENDIX A: GENERATION DATA FOR YEAR 2040	53

APPENDIX B: EXISTING AND UNDER COSTRUCTION TRANSMISSION LINES OF BAGMATI PROVINCE	56

APPENDIX C: ETAP LOAD FLOW MODEL OF BAGMATI PROVINCE	57

APPENDIX D: PROPERTIES OF ACSR CONDUCTOR	58

APPENDIX E: INFLATION ADJUSTMENT FOR LINE COST	59

APPENDIX F: GAMS CODE FOR TRANSMISSION EXPASION PLANNING	60

APPENDIX G: ORIGINALITY REPORT	67

# LIST OF FIGURES

Figure 3.1: Block Diagram of Research Methodology	24

Figure 4.1: Garver 6 Bus Test System	36

# LIST OF TABLES

Table 3.1: Minimum Electrical Clearance between Conductor for different Voltage level	26

Table 3.2: Parameters of Mostly used Conductor types for Various Voltage Levels	29

Table 4.1: Load Demand of Bagmati Province for the year 2040	33

Table 4.2: Result of Load flow analysis for Branch Flow	34

Table 4.3: Result for Inter-Province Power Flow	36

Table 4.4: Input data for Garver 6 Bus Test system	37

Table 4.5: Modified Garver Test System	37

Table 4.6: DC-load flow result for Garver 6 bus System	38

Table 4.7: Result for  Decision Variable and Branch Power Flow  for Garver 6 Bus system	38

Table 4.8: Load and Generation data for Transmission Expansion Planning of Bagmati Province	40

Table 4.9: Result of Decision Variable of Construction of New lines	41

Table 4.10: Power Flow Results for expansion Solution	44

# LIST OF ACRONYMS AND ABBREVIATIONS

AC: Alternating Current

DC: Direct Current

ETAP: Electrical Transient Analyser Program

GAMS: General Algebraic Modeling System

LP: Linear Programming

MILP: Mixed Integer Linear Programming

NEA: Nepal Electricity Authority

TEP: Transmission Expansion Planning

OTEP: Optimal Transmission Expansion Planning

# INTRODUCTION

## Background

The electric power system is composed of various generating sources and load centers which are connected through a network of transmission lines. The purpose of an electrical power transmission network is to transfer power to load centers securely, efficiently, reliably, and economically from generation facilities. For any power system to deliver a dependable and secure electric service a strong transmission network is essential and a strong and reliable network can only be achieved by proper and rational planning of the transmission system.

With the growth in the economy, power demand will also increase. As the demand increases, the existing power system also needs to be expanded which needs careful planning of the electrical transmission network. The expansion planning of a power transmission system involves determining where, when, and how many transmission lines should be built to fulfill prospective demand in the future power system while taking into account a range of operational and economic restrictions (Chebbo, 2000). Hence, high voltage transmission expansion planning is a complex decision-making problem that requires extensive analysis to determine the time, location, type, and number of transmission facilities that are needed in the future power system (Choi, Mount and Thomas 2007).

Finding solutions to expand an existing transmission system while meeting predetermined economic and technical requirements is the major goal of Transmission Expansion Planning (TEP). It involves solving complex non-linear power flow equations subjected to multiple inequalities constraints (Akbari, 2018). Hence, TEP is naturally a large-scale, mixed-integer, nonlinear, and non-convex optimization problem and it is quite difficult to solve and the computation time is extremely long (Hui Zhang et al., 2013).

The main objective of the transmission expansion plan is to find out the least expensive network configuration that can meet the projected power demand of the system without compromising the physical integrity of the network. The problem of transmission expansion planning is often dealt by the engineers trying to find a less expensive option to expand the transmission system, but without solving a formal optimization problem (Seifi et al., 2007).

Because of high uncertainties in the power demand and generation growth, the decisions of expansion of power transmission systems need to be taken carefully as they are in general irrevocable because of their high investment costs (Esmaili et al., 2020).

In the context of Nepal, with the increase in the generation and due to the problems in the evacuation of generated power by the various existing lines in the transmission network, in recent years focus is also shifted toward the transmission system planning. In 2015, a Master Plan for the transmission system of Nepal from the year 2015 to the year 2035 is presented by Nepal Electricity Authority (NEA). Also, an Integrated Master Plan for the evacuation of power from Nepal to India was proposed by the Joint Technical Team (JTT) of Nepal and India to facilitate the export of the energy from the developed hydropowers to India. (RPGCL, 2018).

Since the development of transmission lines requires significantly high investment, optimal transmission expansion planning is essential for a secure and reliable transmission network.

## Rationale and Problem Statement

In the White paper published by the Ministry of Energy, Water Resources, and Irrigation in 2018, the government of Nepal has envisaged developing 15,000 MW of hydropower in 10 years and around 40,000 MW by the year 2040 (MOEWRI, 2018). To evacuate this large volume of generated power to various load centers in the country, a secure and reliable transmission network is required, which means more transmission lines needed to be installed in the existing power system.

Bagmati Province covers the central region of Nepal and consists of 13 districts viz. Dolakha, Sindhupalchok, Rasuwa, Dhading, Nuwakot, Kathmandu, Lalitpur, Bhaktapur, Kavrepalanchok, Makwanpur, Chitawan, Sindhuli, and Ramechhap (GoN, 2015). It is one of the most industrialized Provinces and hosts 4 (Balaju, Bhaktapur, Patan, and Hetauda) out of 11 industrial estates along with three additional Special Economic Zones (SEZ) currently under study and under construction (IDML, 2076). Also, the region is the largest contributor to the national economy with a share of 39.6% of the national GDP, and has the largest per capita income of 2430 USD (CBS, 2021).

The existing transmission facilities in this province consist of transmission lines of voltage levels 66 kV to 400 kV encompassing large and small 40 substations 17 of which are major substations of voltage levels 132 kV to 400 kV (NEA, 2022). Some of the major hydro-projects in the region under planned for the development are: Budhi Gandaki Storage Hydropower Project (1200 MW), Sunkoshi-2 (1110 MW), Sunkoshi-3 (536 MW), and Tamakoshi-3 (650MW). Power generation from hydropower plants and load demand in this region is expected to reach about 6.32 GW and 4.48 GW respectively by the year 2040 (RPGCL, 2018).

Currently, New Dhalkebar-Hetauda section of the 400kV  East-West transmission line is under construction by NEA (NEA, 2022). Similarly, Lamosangu-Lapsiphedi-Ratmate 400kV transmission line is being planned to develop under MCC Nepal (RPGCL, 2018).

In this research, keeping in view the growing power demand and generation expansion in the future of the Bagmati Province, the following research questions are formulated:

- Is the existing transmission system adequate for taking the forecasted load demand for the year 2040?

- How to provide the optimal solution to the transmission expansion of the region through systematic study?

## Objectives

### Main Objective

The main objective of this study is to determine the optimal expansion plan for high voltage transmission lines in Bagmati Province of Nepal considering the generation-demand scenario for the year 2040 AD.

### Specific Objectives

The main objective of the study is guided by the following specific objectives:

- To evaluate the adequacy of the existing electric transmission system of Bagmati Province for the generation-load scenario for the year 2040.

- To formulate a Mixed-Integer Linear Programming (MILP) model for the transmission expansion planning of the Bagmati Province of Nepal using the DC load flow method.

- To determine the optimal transmission system of the Bagmati Province of Nepal based on forecasted data for the year 2040 using formulated MILP Model.

## Limitations

This study shall be constrained by the followings assumptions and limitations:

- The transmission expansion planning model is based on the DC load flow method which does not takes system losses and reactive power flows into account.

- As all the line segments in the province is short length (i.e. below 80 km), line power transfer capability is determined based on the thermal limits of the conductors used.

- System contingency criteria are not considered for the study. That is, the effect of the failure of one or more transmission lines or generating units on the system loading has not been considered in the planning model.

- The static type planning model is considered. That means, the investment dynamics, timeframe, and time worth of money are not taken into consideration.

- Social and environmental cost and cost of land acquisition are not represented in the planning cost parameters. Price variation due to various construction issues such as changes in the route alignment due to urban settlements along the route needs to be checked during the implementation of expansion solution.

# LITERATURE REVIEW

## Background

Transmission network expansion planning (TNEP) is an important research area in power systems. While conducting the literature survey it can be found that the study in this field dates back to the 1970s and it has received extensive attention in recent years. A large amount of research work has been conducted to simplify the problem and alleviate the computational burden.

Garver, in 1970, solved the Transmission Expansion Planning problem by considering the problem with the transportation model and solving it using linear programming to find the shortest route between the generators and the loads. (Garver, 1970)

When similar studies' literature is examined, it becomes clear that the transmission expansion problem is typically categorized based on the following factors: methods for solving the problem, planning horizon, modeling perspective, reliability and uncertainties, coordination between TEP and generation expansion planning (GEP), objective function type, integration of renewable energy sources, and environmental concerns. (Latorre et al., 2003).

## Transmission Expansion Planning Approaches

In General, the Transmission Expansion Planning (TEP)  problem is a large-scale, Mixed integer, non-convex, non-linear problem (Romero & Monticelli, 1994). The best way to solve this type of problem is through mathematical modeling. TEP models, based on the problem solution approach,  can be broadly segregated into: i) optimization models, ii) heuristic models, and iii) meta-heuristic models (Mutlu & Şenyiğit, 2021).

### TEP with Optimization Models

Optimization modeling is more deterministic approach to solve the transmission planning problem. In an optimization model, subject to a certain set of constraints, a specific objective function is defined that must be either minimized or maximized. The objective function is usually defined to reduce the total cost of building new lines, the cost of strengthening of existing transmission lines, and the cost of maintenance of the lines over the specified planning horizon (Lumbreras, 2021).

The main mathematical optimization model used for transmission planning are: a) AC model, b) DC model, and c) transportation model (Dubey et al., 2010). Although they frequently place more stringent conditions on the model that must be optimized, mathematical programming techniques typically ensure the optimality of the solution. (Romero et al, 2003).

Due to incorporation of the reactive power calculations and system losses in the modeling, the AC model is considered to be the most accurate representation of the system (Mahdavi et al., 2018). However, due to non-linearity and non-convex constraints, the AC model is also the most complex and computationally challenging formulation.  Additionally, the AC model's nonlinear properties do not guarantee that the final result is the global optimum.  Because of these drawbacks, DC models, represented with linearized system constraints, are widely used for TEP modeling. With DC model, the TEP problems are easier to solve computationally and also ensure a global optimum results. (Akbari & Tavakoli Bina, 2014) (Farrag et al., 2019).

Deterministic optimization makes the assumption that the facts are accurate for the given task. The deterministic method yields precise and distinctive conclusions. Priority list (PL), linear programming method, Branch-and-Bound (B&B) method, and Lagrangian Relaxation, non-linear programming method are some of the techniques used in this type of modeling (Saravanan et al., 2013).

The fundamental problem with mathematical optimization models is that they frequently involve a significant amount of computer work and provide challenges to handle the expansion of medium and large power systems. In some cases, they may even experience convergence issues. This significant flaw in mathematical optimization models explains why the scientific community chose to use heuristics in addition to mathematics to solve the TEP problem (Henneaux et al., 2016).

Villanasa et al. formulated transmission planning as a simple linear programming (LP) problem with continuous decision variables. They proposed an LP method with continuous variables for optimal transmission planning by minimizing load curtailment (Villasana et al., 1985).

A new approach for solving the real world transmission expansion planning problem with the Benders decomposition technique was proposed by Binato et al. where they used southeastern Brazilian system for the study (Binato et al., 2001).

Natalia Alguacil et al. proposed a mixed integer linear programming approach to solve the long-term, large-scale, transmission expansion static planning problem. Their formulation considered transmission losses in the system, and optimality was guaranteed when solving with the existing optimization softwares (Alguacil et al., 2003).

Khodaei et al. introduced the concept of transmission switching in transmission and generation expansion planning problems. The authors propose a three-step optimization formulation for transmission and generation expansion planning using the Benders decomposition technique, and considered contingency analysis for all existing and candidate lines and integrated transmission switching to alleviate violations in line flows (Khodaei et al., 2010).

A nodal capacity market framework was proposed by Rudkevich (2012) for generation and transmission expansion planning. The author used the flow cancellation technique to represent a fixed list of contingencies in a reliability dispatch formulation, in which all resources are dispatched at zero costs, and load shedding will be penalized at the value of lost load (VOLL) price.

In context of Nepal, Sainju et al. formulated a linear mixed integer planning model. They used the model for solving the Garver 6-bus system and 132 kV network of Attaria-Butwal grid division of INPS. They suggested the future work to accommodate the line losses and different voltage level in the model (Sainju et al., 2016).

In some of the literatures, combined Generation and Transmission Expansion Planning problems are also solved in a dynamic, multi-year, time frame. Fathtabar el. al. proposed  a framework with linearized AC model in Multi Carrier Energy Systems (MCES) for the solution of multi-year combined generation and transmission expansion planning. The results were then compared with that of DC model to establish its effectiveness. (Fathtabar el. al., 2018).

Aming to reduce the impact of a cascading failure, S. Armaghani et. al. introduced pseudo-dynamic, multi-stage/year Transmission Expansion Planning using a initiative process. They identified the most critical line based on its ability to initiate and propagate a cascading failure in a network and reinforcements of the entire network was performed (S. Armaghani, 2020).

### TEP with Heuristics Models

The contemporary replacement for mathematical optimization models is heuristic approaches. Heuristics are all methods that develop solutions incrementally rather than addressing an optimization problem. These processes carry out local searches up until they are unable to locate a better answer; they then invoke the satisfaction of predetermined stopping criteria to halt the search. Heuristics, as opposed to quantitative optimization models, are thereby streamlined processes for finding workable solutions to complicated issues.

Heuristics methods do not always find the best expansion plan, especially when they are applied to real-world power systems, despite the fact that they do return feasible solutions fairly quickly. They also do not, mathematically speaking, provide bounds or proofs on the quality or optimality of their solutions. (Raider et al., 2008).

Moreno et al. (2013) employed a probabilistic method for the determination of transmission investment and operation cost by incorporating the system contingencies and corrective measure into operation cost estimation. Generation reserves and special protection schemes are considered additional corrective actions that can help system stability during contingencies and decrease operation costs by reducing load shedding.

## Based on Planning Horizon

The transmission Expansion Planning approach can be classified as static or dynamic based on the handling of planning periods. In static transmission expansion planning, the problem is analyzed to figure out where the power lines should be expanded to meet the future demand considering a single planning period. Thus, the planning horizon is taken into account at once (Kaur et al., 2017).

In the dynamic planning approach, the planning horizon is divided into several sub-periods and the expansion decision and investment planning is analyzed over these sub-periods. It should be noted that a heavier computational effort is required for the multiyear consideration of investment decisions regarding the expansion planning which often becomes prohibitive when solved using the commercial solver. However, this approach can provide better solution because it is possible to obtain solutions that can anticipate the installation of new lines or strengthening of the existing lines to reduce the involved costs in terms of time value of money (Slednev et al., 2017).

## Methods and Tools for Transmission System Planning

### Consideration in Design of Transmission Line

For a given power to be transmitted over a given distance, a suitable line is selected based on the economic voltage level and selection of the economic size of the conductor.

The preliminary estimate for economic line Voltage is given by the following empirical formula given by “Power System Analysis and Design” (Gupta, B.R. , 2008):

| V = 5.5 (L6+PNc*Cosϕ*100)^0.5 | Eq. 2.1 |
| --- | --- |

Where,

V= line voltage in kV

L=distance in km

P= power to be transmitted in kW

Nc= No. of Circuits

Cos( ϕ) = Power factor

Selection of the economic size of the conductor is based on the continuous current carrying capacity and efficiency criteria. Overhead transmission line uses invariably the ACSR conductor.

The power transmission capacity of the lines in  MVA is calculated using the formula:

| Pmax= 3 V.I/1000 | Eq. 2.2 |
| --- | --- |

Where,

Pmax= Maximum apparent power transfer capacity of  a line in MVA

V= Line voltage in kV

I = Line current in Amp

### Load Flow Methods

The solution to any Transmission planning problem involves the solution of load flow equations. The classical load flow problem requires considering four variables at each bus “i” of a power system. These variables are:

1. Pi( active power injection)

2. Qi(Net reactive power injection)

3. Vi(Voltage magnitude)

4.  α (Voltage angle)

The AC power flow model uses the exact expressions of the power flow equations based on Kirchhoff's current law where the active and reactive power injections at each bus i are calculated as follows:

| Pi=Vij=1nVj.Yij.Cos⁡(θi-θj-γij) | Eq. 2.3 |
| --- | --- |

| Qi=Vij=1nVj.Yij.Sin(θi-θj-γij) | Eq. 2.4 |
| --- | --- |

Where,

θi , θj = Voltage angle at bus i, and j respectively

γij = line admittance angle of line connected between bus i and j

The above equations (2.3) and (2.4) are known as the static load flow equations. These equations are non-linear therefore can only be solved through numerical iterative solutions.

DC power flow model is a linearized, approximated model of the AC power flow model which considers only the real or active power flow in the power system while neglecting the transmission losses.

The following key assumptions were made while approximating the AC load flow equations into the DC power flow model:

- The series resistance ‘r’ of the line is neglected

- The reactive power flow in the line is not considered

- The voltage angle is small so that sinθ ≈ θ

- The bus voltage magnitudes are assumed to be 1.0 p.u

Based on the above assumptions the ac power flow equation between bus ‘i' and bus ‘j’ is approximated as follows:

| Pij = (θi – θj )/ xij | Eq. 2.5 |
| --- | --- |

Where Pij = Active power flow from bus i to j (in per unit)

θi , θj = voltage angle of bus i and j

xij = line reactance between bus i and j (in per unit)

Although the DC model does not represent accurately the AC power system as it neglects the system reactive power flow and line losses, it is computationally less complex. Furthermore, in comparison to the AC formulation, which may lead to a locally optimal solution, the DC power flow formulation represented by a linear objective function along with a set of linear constraints, guarantees a global optimum solution (Zhang et al., 2012).

### Mixed-integer Linear Programming

The mathematical modeling method known as mixed integer linear programming (MILP) is useful for resolving challenging optimization issues. The method has many applications in operations research, including energy system optimization and planning for the expansion of power transmission systems. An integer linear programming (ILP) problem is created when some (or all) of the variables in an LP problem are limited to assuming only integer values.

Mixed integer programming adds one extra requirement that at least one of the variables can only take on integer values. The mathematical representation of the mixed integer programming (MIP) problem is as follows:

Maximize (or minimize)

| Z = C .X | Eq. 2.6 |
| --- | --- |

subject to

AX ≤ b,

X ≥ 0,.

Where, X= [ x1, x2,….xn], decision variables (the unknowns)

C = [c1, c2,…..cn], constants

b = [b1, b2,….bn], bound constraints

Although, it is simple to express integrality constraints for a problem when modeling it, doing so frequently makes the problem more difficult (and perhaps impossible) to solve. Relaxing, or ignoring, the integrality constraints and solving the issue as if it were a typical LP issue where all the variables are taken to be continuous, is one method for determining the best integer solution to a problem.

A branch-and-bound approach based on linear programming is typically used to handle mixed integer linear programming issues. Theoretically, using the B&B algorithm, we can answer every ILP problem by resolving a set of LP problems known as candidate problems.

## Literature insights and identified gaps

From the above literature review, it can be seen that so far only a few studies have been done in the academic sector about the transmission expansion planning of Nepal. Only a few kinds of literature have endeavored to exploit the advantages of various scientific approaches in the transmission expansion planning of Nepal. Sainju et. al. opted to determine the optimal network configuration for a part of Nepal’s grid power system using the static mixed integer linear programming method. They confided their study only to the Attaria-Butwal grid division of the Integrated Nepal Power System focusing on the 132 kV voltage level (Sainju et al., 2016). Further, the transmission expansion planning models developed in most of the literatures are for the expansion planning of single voltage level only.

This research would be unique to provide the transmission expansion planning methodology for the planning of real power system while considering the different voltage level in the expansion planning solution.

# RESEARCH METHODOLOGY

## Research Methodology

Before commencing any research, developing a research methodology is the first step. To fulfill the objective of this study, a research framework as shown in figure 3.1 is adopted. The study methodology consists of issues identification, critical study of past literature in the field, and analytical model development, and discussion of results followed by conclusion and recommendation.

Figure 3.1: Block Diagram of Research Methodology

### Issue Identification

The main issue of this study is to find the optimal transmission expansion plan for the Integrated Nepalese Power system focusing on the forecasted demand for the year 2040.

### Literature survey

A literature survey has been carried out to study the past work that. Survey is condected to find the extent of the past researches on the field. Approaches and methods for tackling the transmission expansion problem are reviewed.

### Data collection

In transmission expansion planning, it is necessary to have all the required input data at the very beginning of the planning. The planner should have at least the following data beforehand:

- Forecasted Load and Generation data for future years

- Network data of existing Transmission system

- The investment cost data of different types of lines

- Technical parameters of the various types of transmission lines (line resistance, reactance, cost per km, power transmission capacity)

The load forecast data and generation data for the year 2040 are sourced from Rashtriya Prasaran Grid Company Limited (RGPCL, 2018). The data of the existing network is sourced from Nepal Electricity Authority (NEA, 2021). Various technical manuals, codes, articles, and manufacturers’ data sheets are referred to the various technical parameters of different types of transmission lines.

### Load flow Analysis of Existing System

The adequacy of the existing transmission networks for catering the forecasted load demand for year 2040 is evaluated by running a static load flow analysis in the software ETAP (Electrical Transient Analyzer Program). Currently under construction lines are also taken into account while running the load flow analysis.

In ETAP while modeling the transmission lines of different voltage levels, the minimum ground clearance and minimum phase to phase clearance  is referenced from that specified in the manual “COMPENDIUM OF TESTED TOWER DESIGNS FOR EHV TRANSMISSION LINES” (CEA, 2018).  The vertical and horizontal spacing between the conductors in the line of different voltage is given in the Table 3.1 below.

Table 3.1: Minimum Electrical Clearance between Conductors for different Voltage level

| Line Voltage (kV) | No of Circuit | Minimum electrical Clearance between Conductor (in meter) |  |
| --- | --- | --- | --- |
|  |  | Vertical | Horizontal |
| 66 | 1 or 2 | 2 | 3.5 |
| 132 | 1 or 2 | 3.9 | 6.8 |
| 220 | 1 (Horizontal) | - | 6 |
| 220 | 2 | 4.9 | 8.4 |
| 400 | 1 (Horizontal) | - | 11.3 |
| 400 | 2 | 8 | 13-16 |

Further the transmission network of this province is also connected with the substations of other provinces. The Matatitha substsaion is connected to the Marshyandi Substion of Gandaki Province via 220 kV double circuit lines and New-Khimti 220 kV substation and Hetauda 400 kV substations are further connected from the 220 kV double circuit line to the Dhalkebar substation of Madhesh Province.

The interconnection with the substations of the other provinces is represented by a grid/utility representation in ETAP having short-circuit MVA of respective voltage level based on their fault level. MVAsc value (based on a certain fault level) is the representation of the stiffness of a grid. Selection of a higher value of fault level than the actual value will surely affect the fault level at various busbars during short circuit condition however the steady state power flow remains the same. To verify the same, simulation was run by applying the various fault levels ranging from 10 kA to 60 kA while representing the interconnecting grid substation, the results for inter-provincial power flow was observed.

The MVA short-circuit capacity of 19050 MVAsc and 43650 MVAsc is calculated to represent the grid having voltage level 220 kV and 400 kV respectively considering the fault level of 50 kA/1 sec and 63 kA/1 sec for 220 kV and 400 kV voltage levels respectively (CEA, 2013).

Newton-Rapson method is used for the analysis.

The detailed single line diagram representation of the high voltage transmission system of Bagmati Province is shown in APPENDIX-C.

### Method selection and Model development

There are a variety of models and considerations when formulating a TEP problem. In this study, MILP formulation based on the DC Optimal Power Flow (OPF) is used for optimization modeling.

In this study, the transmission expansion planning problem is dealt with a mixed-integer linear programming approach. The proposed transmission expansion planning model considers only the steady state of the network and adopts the linearized active power flow instead of the non-linear power flow due to the following reasons:

- Due to the low value of resistance-to-reactance (R/X) ratio of overhead transmission lines, the linearized model provides a good approximation  for power flows  in high voltage transmission networks  (Westerberg et al., 1977);

- It avoids convergence problems with multiple local minima that are common in non-linear power flow calculations (Zhang et al., 2012).

### Transmission Expansion Planning Model Formulation

To systematically solve the problem of transmission expansion problem, a mathematical model is suggested.

The transmission system expansion planning problem is formulated as a mixed integer linear programming optimization problem that simulates the power flow in the transmission network into mathematical equations.

To have a linear optimization model, the network power flow equations are based on the DC load flow formulation. This means at all the buses a voltage magnitude of 1 per unit is assumed. Furthermore, the transmission system expansion planning problem is solved for a one-period horizon, i.e. a static planning methodology is adopted.

The objective function of the problem is to minimize the total investment cost associated with the expansion plan subject to constraints that assure the transmission capacity for load supply. Mathematically, the optimization problem is formulated as follows:

Objective function:

The objective function is defined to minimize the total investment cost.

i.e.,

Minimize

| Z = i,j∈Nk∈TLCk*lij*u(i,j,k) | Eq. 3.1 |
| --- | --- |

Where,

i,j = Index of network buses ( i for sending end and j for receiving end)

N= set of all available buses

TL= set of all  line types for various Voltage level

Ck = Investment cost Per Unit length for line type k ($/km)

lij = Line length between buses i and j

u(i,j,k)= binary decision variable for the construction of line type k between buses i and j

k= index for high voltage line types based on voltage level and conductor used

Based on the types of conductor mostly used in the exising high voltage transmission network of Nepal from the voltage level 66 kV to 400 kV, eight (8) different sets of lines types are selected to represent the existing lines in the network  and prospective lines for the expansion planning.

As per the yearbook published by Nepal Electricity Authority in 2021, the mostly used conductors used in high voltage transmission system of Nepal are:

- For 66 kV voltage level- “Wolf” ( Nominal conductor area- 150 sq. mm)

- For 132 kV voltage level- “BEAR” ( Nominal conductor area- 250 sq. mm) – about 70 % of existing transmission lines in Nepal

- For 220 kV voltage level- “ Twin Bison” (Nominal conductor area -350 sq. mm per conductor) and “Twin Moose” ( Nominal conductor area- 500 sq. mm per conductor)

- For 400 kV voltage level- “ Twin Bison” (Nominal conductor area -350 sq. mm per conductor) and “Twin Moose” ( Nominal conductor area- 500 sq. mm per conductor)

The technical parameter of the above-listed conductor for a given voltage level is presented in Table 3.2.

Table 3.2: Parameters of Mostly used Conductor types for Various Voltage Levels

| Nominal Line Voltage (kV) | No. of circuit | Conductor Code Name | Sub - conductor per pahse | Current carrying capacity at 75 C | Reactance / phase /km | Max. cap. (MVA) | Cost per km | Line type index ‘k’ |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 66 | 1 | Wolf | 1 | 355 | 0.008848 | 40.58 | 0.17 | 1 |
| 66 | 2 | Wolf | 1 | 355 | 0.004425 | 81.16 | 0.20 | 2 |
| 132 | 1 | Bear | 1 | 481 | 0.002216 | 109.9 | 0.26 | 3 |
| 132 | 2 | Bear | 1 | 481 | 0.001236 | 219.9 | 0.29 | 4 |
| 220 | 2 | Twin Bison | 2 | 595 | 0.0003114 | 906.9 | 0.60 | 5 |
| 220 | 2 | Twin Moose | 2 | 763 | 0.0003061 | 1163 | 0.63 | 6 |
| 400 | 2 | Twin Moose | 2 | 763 | 0.0001923 | 2114.55 | 0.89 | 7 |
| 400 | 2 | Quad Moose | 4 | 763 | 0.0001582 | 4229.1 | 0.97 | 8 |

Although the line loadabilty is limited by thermal, voltage regulation, and stability limit depending upon the line length, here maximum power transfer capability expressed in the above table is based on the thermal limit of the conductor only as all the line segments in the province are short lines having line length below 80 km.

Here the current carrying capacity of the conductor at 75 deg. C is based on the ambient temperature of 40 deg. C. The detailed electrical and mechanical properties of the ACSR conductors conforming to BS 215: part 2/1970 is attached in Appendix D.

The value of line reactance is based on the 100 MVA base and is taken from “Manual on Transmission Planning Criteria, Central Electricity Authority, New Delhi” (CEA, 2013).

Line cost per kilometer data is referenced from “Transmission System Development Plan of Nepal, Rastriya Prasaran Grid Company Limited, Nepal” (RPGCL, 2018). The cost/km data mentioned in the Table 3.2 is  after making the adjustment for the inflation taking the Consumer Price Index (CPI) of “Non –food and Service” sector as reference. The following formula is employed for inflation adjustment:

Real price in current year= (CPI in current year/ CPI in base year)*Price in base year

The National Consumer Price Index (CPI) of Nepal for the fiscal year 2018/19 is taken as base year and the CPI of fiscal year 2021/22 is taken as current year.  The detail of cost adjustment for inflation is mentioned in the Appendix E.

This objective function represented by eq. (3.1) is subjected to the following constraints:

- Real power conservation at each node:

At each bus, the total power generated should be equal to the net power flowing out to the other connected buses and the total demand on that bus.

i.e.,

| g∈GiPg-i,j∈NiPij-Di=0 | Eq. 3.2 |
| --- | --- |

Where,

Gi= Set of all generators connected to the bus i

G= domain of a set of all generators

Ni= set of all lines connected to the bus i

Pij= Line flow between bus i and j,

Di = Demand at bus i

- Line  flow constraints:

The powers flowing in existing transmission lines are determined by the equality constraint (3.3). Further, the power flow in the existing line and candidate lines shall be limited by their thermal loading limits as defined by equations (3.4) and (3.7)

| Pij = bijk * (δi – δj) | Eq. 3.3 |
| --- | --- |
| - Pijmax ≤Pij≤ Pijmax | Eq. 3.4 |

Where,

bijk= Susceptance of the line type ‘k’ connected between buses i an j

Pijmax = Maximum thermal loading capacity of the line between i and j

Similarly, the power flow in the candidate line is given by the following equation (4.5)

| Pijk = ui,j,k . bijk * (δi – δj) | Eq. 3.5 |
| --- | --- |

The equation (3.5)  is non-linear in nature as it has terms that contain two variables i.e discrete decision variable u(i,j,k) and voltage angle at bus i (or j) δi (or δj). This non-linear qualities equation represented by equation (3.5) can be transferred into linear inequalities by using a disjunctive parameter M, where  M  is a large positive parameter. This method of linearization has been well studied and described by (Akbari & Tavakoli Bina, 2014), (Kazemi & Ansari, 2022),  (Correa et al., 2014) and (Garcés et al., 2009). This parameter M is large enough so that the bus angle difference between any buses is enforced within an acceptable range regardless if there exists a transmission line between these two buses as formulated  by (3.6)

| - (1-u(i,j,k))M≤Pijk- bij*(δi – δj) ≤ (1-u(i,j,k))M | Eq. 3.6 |
| --- | --- |
| - Pijmax. u(i,j,k) ≤ Pij ≤ Pijmax u(i,j,k) | Eq. 3.7 |

Here the appropriate value for Big M parameter as suggested by (Soroudi, 2017) is :

| M=Max [bijk.δi – δj] | Eq. 3.8 |
| --- | --- |

- Generator dispatch Limits

The upper limit and lower limit of generators are governed by their output capacity and represented by the inequality equation (3.9)

| Pgmin ≤ Pg ≤ Pgmax | Eq. 3.9 |
| --- | --- |

- Angle constraints

| ∆δijmin ≤ (δi – δj) ≤ ∆δijmax | Eq. 3.10 |
| --- | --- |
| δref = 0 | Eq. 3.11 |

Where,

δref = Voltage angle of reference or slack bus

- Decision variable

A binary variable is used for determining the selection  of candidate lines between substaions which is represented by the equations (3.12)

| u(i,j,k) ∈{0,1} | Eq. 3.12 |
| --- | --- |

Where,

u(i,j,k) = Binary decision variable: u(i,j,k)=1 if line type k is built; u(i,j,k)=0 if not

### Tools Selected

To run the load flow analysis to evaluate the capacity of the existing system based on the generation and load data of the specified planning horizon, an Electrical Transient Analyser Program (ETAP) software is selected.  ETAP is a very software and fully graphical electrical power system analysis program for power system studies.

General Algebraic Modeling System (GAMS) is selected to solve the optimization problem of transmission line expansion planning. GAMS is high-level modeling software for mathematical programming and optimization and is specially designed to solve large and difficult linear, non-linear and mixed-integer optimization problems quickly. The solver used for the optimization process is CPLEX.

### Model Writing and Model Testing

The mathematical optimization model thus formulated is coded in GAMS software. In the developed model, any line between two buses can be represented by one of the eight sets of line types. These line types are based on the voltage level to be selected and different types of a conductor in the given voltage level between 66 kv and 400 kV.

The program written in GAMS to solve the transmission expansion planning problem is attached in APPENDIX F.

Before simulating the data of Bagmati province, first, the model thus developed is tested. The program is tested using Garver’s 6 bus test system.

# RESULTS AND DISCUSSION

## Load Flow Analysis of Existing Transmission System

The main thesis work starts with the analysis of the adequacy of the existing transmission system of Bagmati Province of Nepal to handle the demand and generation for the year 2040. For this, a static load flow analysis is performed by taking the data of existing transmission facilities and load and generation data of the year 2040.

The Load forecast data for the Bagmati Province shows a total demand of the the region is expected to reach about 4880 MW. The major load centers supplying the power to various domestic, commercial, industrial, and transportation loads in the region are Hetauda, Balaju, and Matatirtha where demand is forecasted to reach 2250 MW, 400 MW, and 550 MW respectively. (RPGCL, 2018).

The detail of forecasted load data of Bagmati Province for the year is presented in Table 4.1.

Table 4.1: Load Demand of Bagmati Province for the year 2040

| S.N | Substation | Load (MW) | Total |
| --- | --- | --- | --- |
|  | Khimti | 260 |  |
|  | Bahrabise | 50 | 4880 |
|  | Bhaktapur | 220 |  |
|  | Mulpani | 200 |  |
|  | Balaju | 400 |  |
|  | Chapali | 150 |  |
|  | Harisidhi | 300 |  |
|  | Matatirtha | 550 |  |
|  | Suichatar | 150 |  |
|  | Trishuli | 200 |  |
|  | Ratmate | 150 |  |
|  | Hetauda | 2250 |  |

The Bagmati province will have a generation capacity of 6315 MW from various hydropower projects. Budhi Gandaki storage (1200 MW), Upper Tamakoshi (456 MW), Upper Trisuli-1 (216 MW), Khimti Shivalaya storage (200 MW), and Langtang reservoir (300 MW) are the major generating station for this region. The details of generation data of Bagmati Province for year 2040 is given in APPENDIX-A.

The detail datat of existing  and under-constrution transmission lines of  bagmati Province is data is attached in APPENDIX-B.

The load flow analysis result considering Budhi Gandaki HEP (1200 MW) as a swing bus is presented in Table 4.2.

Table 4.2: Result of Load flow analysis for Branch Flow

| From |  | To |  | MW Flow | Mvar Flow | MVA Flow | Line MVA Capacity | % Line Loading |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bus no. | Bus name | Bus no | Bus name |  |  |  |  |  |
| 1 | NewKhimti 400 | 2 | Bahrabise 400 | 106.03 | -56.136 | 119.969 | 4229.10 | 2.84% |
| 2 | Bahrabise 400 | 3 | Lapsephedi 400 | 267.98 | 25.148 | 269.152 | 4229.10 | 6.36% |
| 3 | Lapsephedi 400 | 5 | Ratmate | 114.84 | -144.19 | 184.336 | 4229.10 | 4.36% |
| 31 | Lapsephedi 132 | 18 | Bhaktapur 132 | 174.17 | 206.36 | 270.038 | 219.95 | 122.77% |
| 4 | Lamosangu | 18 | Bhaktapur 132 | 587.73 | 357.144 | 687.734 | 219.95 | 312.68% |
| 5 | Ratmate | 40 | Hetauda 400 | 1090.4 | -97.87 | 1094.8 | 4229.10 | 25.89% |
| 6 | Chilime HEP | 10 | Trisuli HEP | 22 | 0 | 22 | 40.58 | 54.21% |
| 10 | Trisuli HEP | 11 | Devighat | 37.426 | 13.304 | 39.7203 | 40.58 | 97.87% |
| 10 | Trisuli HEP | 33 | Balaju 66 | 6.944 | -0.967 | 7.01101 | 40.58 | 17.28% |
| 11 | Devighat | 34 | Chapali 66 | 50.81 | 20.84 | 54.9178 | 40.58 | 135.32% |
| 14 | Chapali 132 | 12 | Balaju 132 | 192.68 | -22.17 | 193.949 | 219.95 | 88.18% |
| 34 | Chapali 66 | 15 | Chabel | -52.72 | -30.77 | 61.0382 | 81.17 | 75.20% |
| 14 | Chapali 132 | 17 | Mulpani | -231.3 | -45.59 | 235.726 | 219.95 | 107.17% |
| 15 | Chabel | 16 | Lainchaur | -53.33 | -31.725 | 62.0555 | 40.58 | 152.91% |
| 16 | Lainchaur | 33 | Balaju 66 | -55.4 | -37.4 | 66.8425 | 40.58 | 164.71% |
| 12 | Balaju 132 | 13 | Suichatar 132 | -234.1 | -280 | 364.957 | 109.97 | 331.86% |
| 33 | Balaju 66 | 35 | Suichatar 66 | -34.73 | -27.69 | 44.4174 | 81.17 | 54.72% |
| 35 | Suichatar 66 | 23 | Teku | 0 | -0.048 | 0.048 | 219.95 | 0.02% |
| 23 | Teku | 24 | K3 SS | 0 | -0.019 | 0.019 | 81.17 | 0.02% |
| 17 | Mulpani | 18 | Bhaktapur 132 | -432.7 | -173.113 | 466.031 | 219.95 | 211.88% |
| 35 | Suichatar 66 | 20 | Patan | -26.02 | -2.917 | 26.187 | 81.17 | 32.26% |
| 20 | Patan | 19 | Baneshwor | -26.24 | -3.16 | 26.4306 | 40.58 | 65.13% |
| 19 | Baneshwor | 32 | Bhaktapur 66 | -26.42 | -3.46 | 26.6456 | 40.58 | 65.66% |
| 13 | Suichatar 132 | 36 | Matatirtha 132 | -456.3 | -490.852 | 670.169 | 219.95 | 304.69% |
| 35 | Suichatar 66 | 25 | Kulekhani-I | -97.05 | -40.4 | 105.123 | 81.17 | 129.52% |
| 22 | Matatirtha 220 | 8 | Trisuli3B 220 | -1305 | 369.935 | 1356.22 | 1163.00 | 116.61% |
| 37 | Trisuli3B 132 | 9 | Samundratar | -264.8 | 31.94 | 266.737 | 219.95 | 121.27% |
| 8 | Trisuli3B 220 | 7 | Chilime220 | -807.5 | 134.153 | 818.607 | 906.93 | 90.26% |
| 36 | Matatirtha 132 | 26 | Kulekhani-II | -238.4 | -137.72 | 275.31 | 219.95 | 125.17% |
| 26 | Kulekhani-II | 27 | Hetauda 132 | -220.3 | -152.61 | 268.021 | 219.95 | 121.86% |
| 25 | Kulekhani-I | 21 | Hetauda 66 | -30.91 | -14.25 | 34.0366 | 81.17 | 41.93% |
| 27 | Hetauda 132 | 28 | Bharatpur 132 | -46.3 | -22.86 | 51.6368 | 219.95 | 23.48% |

Table 4.4 shows that for the given load and generation scenario of the year 2040, 14 out of 32 lines (branch) are overloaded beyond their rated capacity. The result shows the Lamosangu- Bhaktapur 132 kV double circuit line, Lapsephedi- Bhaktapur 132 kV double circuit line, Balaju-Suichatar 132 kV single circuit lines, and Suichatar- Matatirtha 132 kV lines are overloaded by more than double their capacity.

The analysis also provides the result for inter-province power flow to the various substation of other provinces connected to the Bagmati Province. The result for out-of-province power flow is shown in Table 4.3.

Table 4.3: Result for Inter-Province Power Flow

| From | To | MW flow | MVAr flow | MVA Flow |
| --- | --- | --- | --- | --- |
| Matatirtha 220 | Marsyandi 220 (Gandaki Province) | 529.66 | -141.33 | 548.19147 |
| Hetauda 400 | Dhalkebar 400 (Madhesh Province) | -1340.8 | -1637.38 | 2116.3076 |
| Khimti 220 | Dhalkebar 220 (Madhesh Province) | 2236.51 | -77.79 | 2237.8624 |
| Bharatpur 220 | New Butwal 220 (Lumbini Province) | -47.37 | -25.27 | 53.688824 |

This result of the static load-flow analysis clearly shows that transmission expansion planning is needed to solve the problem of the overloading of the various lines while catering to the demand for the year 2040.

## Garver’s 6 bus test system

The Garver’s 6 bus test system is one of the mostly used test system in transmission expansion planning researches. The system has 6 buses, 15 right-of-ways for the addition of new circuits where the total demand is 760 MW and the total generation capacity is equal to 1110 MW. The configuration of for Garver 6-bus system is shown in figure 4.2.

Figure 4.1: Garver 6 Bus Test System

All detailed parameters regarding this system are reported in the published work (Garver, 1970) which is also presented in Table 4.4 below.

Table 4.4: Input data for Garver 6 Bus Test system

| From | To | X (pu) | Capacity (MVA) | Cost (MUSD) | Line Status |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 0.4 | 100 | 40 | 1 |
| 1 | 3 | 0.38 | 100 | 38 | 0 |
| 1 | 4 | 0.6 | 80 | 60 | 1 |
| 1 | 5 | 0.2 | 100 | 20 | 1 |
| 1 | 6 | 0.68 | 100 | 68 | 0 |
| 2 | 3 | 0.2 | 100 | 20 | 1 |
| 2 | 4 | 0.4 | 100 | 40 | 1 |
| 2 | 5 | 0.31 | 100 | 31 | 0 |
| 2 | 6 | 0.3 | 100 | 30 | 0 |
| 3 | 4 | 0.59 | 80 | 59 | 0 |
| 3 | 5 | 0.2 | 100 | 20 | 1 |
| 3 | 6 | 0.48 | 100 | 48 | 0 |
| 4 | 5 | 0.63 | 75 | 63 | 0 |
| 4 | 6 | 0.3 | 100 | 30 | 0 |
| 5 | 6 | 0.61 | 80 | 61 | 0 |

To test the model using the Garver test system data, some modification in the Garver six bus is made while keeping the original data of the test system intact. The data for the modified Garver six bus model is presented in Table 4.5.. The existing line capacity of the Garver test system is similar to a single circuit 132 kV line having a maximum power transfer capacity of 110 MVA. Taking the reactance values of these lines, cost parameter and line length parameters are assigned.

Table 4.5: Modified Garver Test System

| From | To | X (pu) | x/km | Capacity | Status | Length (km) | Cost/km |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 0.4 | 0.002216 | 100 | 1 | 180.51 | 0.2216 |
| 1 | 3 | 0.38 | 0.002216 | 100 | 0 | 171.48 | 0.2216 |
| 1 | 4 | 0.6 | 0.002216 | 80 | 1 | 270.76 | 0.2216 |
| 1 | 5 | 0.2 | 0.002216 | 100 | 1 | 90.25 | 0.2216 |
| 1 | 6 | 0.68 | 0.002216 | 72 | 0 | 306.86 | 0.2216 |
| 2 | 3 | 0.2 | 0.002216 | 100 | 1 | 90.25 | 0.2216 |
| 2 | 4 | 0.4 | 0.002216 | 100 | 1 | 180.51 | 0.2216 |
| 2 | 5 | 0.31 | 0.002216 | 100 | 0 | 139.89 | 0.2216 |
| 2 | 6 | 0.3 | 0.002216 | 100 | 0 | 135.38 | 0.2216 |
| 3 | 4 | 0.59 | 0.002216 | 80 | 0 | 266.25 | 0.2216 |
| 3 | 5 | 0.2 | 0.002216 | 100 | 1 | 90.25 | 0.2216 |
| 3 | 6 | 0.48 | 0.002216 | 100 | 0 | 216.61 | 0.2216 |
| 4 | 5 | 0.63 | 0.002216 | 80 | 0 | 284.3 | 0.2216 |
| 4 | 6 | 0.3 | 0.002216 | 100 | 0 | 135.38 | 0.2216 |
| 5 | 6 | 0.61 | 0.002216 | 80 | 0 | 275.27 | 0.2216 |

Using the developed algorithm and above data, the Garver 6 bus test system is analyzed. The DC-load flow result for the modified Garver system is  presented in Table 4.6:

Table 4.6: DC-load flow result for Garver 6 bus System

| Bus | Generation | Voltage Angle | Load |
| --- | --- | --- | --- |
| 1 | 150 |  | 80 |
| 2 |  | 0.027 | 240 |
| 3 | 310 | 0.118 | 40 |
| 4 |  | -0.368 | 160 |
| 5 |  | -0.031 | 240 |
| 6 | 300 | 0.327 |  |

Further, the result for the expansion planning decision variables along with line flow is presented in Table 4.7.

Table 4.7: Result for  Decision Variable and Branch Power Flow  for Garver 6 Bus system

| From | To | Existing line type | Result from the Planning model |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | LT1 (Cap: 100 MVA) | LT2 (Cap: 200 MVA) | LT3 (Cap: 300 MVA) |
| 1 | 2 | 1 | dV= 1; P12= (-6.836) | dV=0 | dV=0 |
| 1 | 3 | 0 |  | dV=0 | dV=0 |
| 1 | 4 | 1 | dV= 1; P14= 61.266 | dV=0 | dV=0 |
| 1 | 5 | 1 | dV= 1; P15= 15.569 | dV=0 | dV=0 |
| 1 | 6 | 0 |  | dV=0 | dV=0 |
| 2 | 3 | 1 | dV= 1; P23= -45.569 | dV=0 | dV=0 |
| 2 | 4 | 1 | dV= 1; P24= 98.734 | dV=0 | dV=0 |
| 2 | 5 | 0 | dV=0 | dV=0 | dV=0 |
| 2 | 6 | 0 | dV=0 | dV=0 | dV= 1; P26= -300.00 |
| 3 | 4 | 0 | dV=0 | dV=0 | dV=0 |
| 3 | 5 | 1 | dV= 1; P35= 74.810 | dV= 1; P35= 149.62 | dV=0 |
| 3 | 6 | 0 | dV=0 | dV=0 | dV=0 |
| 4 | 5 | 0 | dV=0 | dV=0 | dV=0 |
| 4 | 6 | 0 | dV=0 | dV=0 | dV=0 |
| 5 | 6 | 0 | dV=0 | dV=0 | dV=0 |

In the above Table, the term dV represents the decision variable. The value dV= 1 means the perspective line is to be built and dV=0 means not to build to the line.

The total cost of the transmission planning is found to be  129.89 Million USD. The result from the developed model is compared with the result reported by Alguacil et al., (2003). They reported that 2 no of lines should be built on 2-6 corridor, one no of the line should be added in 3-5 corridor and 2 no. of lines should be built on 4-6 corridor; each new line should have power transfer capacity 100 MVA.  According to their research, the total expansion cost would be 140 MUSD.

However, this study suggests building one line having a capacity of 200 MVA should be added to the corridor 3-5, and one line having a capacity of 300 MVA should be added in 2-6 corridors which results in a total expansion cost of 129.89 Million USD.

## Bagmati Province High Voltage Transmission Expansion Planning

After successfully testing the developed program, simulation is run for the data of Bagmati Province of Nepal for high voltage and extra high voltage transmission systems. Generation and demand connected to the various substation for the year 2040 is adjusted also considering the inter-provincial power flow as determined by the static load flow analysis.

The adjusted load and generation data at various buses is presented in Table 4.8.

Table 4.8: Load and Generation data for Transmission Expansion Planning of Bagmati Province

| Bus no. | Bus Name | Generation (MW) | Load (MW) | Remarks |
| --- | --- | --- | --- | --- |
| 1 | NewKhimti | 2226.56 | 2496.51 | 2236.51 MW is added as load to this bus representing the power flow going to Dhalkebar Substation as determined by Static Load flow analysis. |
| 2 | Bahrabise | 423.82 | 50 |  |
| 3 | Lapsephedi | 22.9 | 0 |  |
| 4 | Lamosangu | 587 | 0 |  |
| 5 | Ratmate | 1305.67 | 150 |  |
| 6 | Chilime | 822 | 0 |  |
| 7 | Trisuli3B |  | 200 |  |
| 8 | Samundratar | 279 | 0 |  |
| 9 | Balaju | 60.1 | 400 |  |
| 10 | Suichatar | 82 | 450 |  |
| 11 | Chapali | 0 | 150 |  |
| 12 | Mulpani | 0 | 200 |  |
| 13 | Bhaktapur | 17.5 | 220 |  |
| 14 | Matatirtha | 0 | 1079.66 | 529.66 MW is added load to this bus representing the power flow going to the Marsyandi Substation of Gandaki Province. |
| 15 | Kulekhani-II | 32 | 0 |  |
| 16 | Hetauda | 27.04 | 2250 | 1340.8 MW is added as a generation coming from Dhalkebar Substation of Madesh Province as determined by Static Load flow analysis |
| 17 | Bharatpur | 47.37 | 0 | 47.37 MW is added as a generation coming from New butwal Substation of Lumbine Province as determined by Static Load flow analysis |
| 18 | Kulekhani-1 |  |  |  |
| 19 | Patan | 0 | 150 |  |
| 20 | Baneshwor | 0 | 0 |  |
| 21 | Chabel | 0 | 0 |  |
| 22 | Lainchaur | 0 | 0 |  |
| 23 | Trisuli HEP | 24 | 0 |  |
| 24 | Devighat HEP | 14 | 0 |  |
| 25 | ChilimeHEP | 22 | 0 |  |

The result given by the model for decision variable i.e. for the selection of optimal transmission line between various buses are presented in the Table 4.9.

Table 4.9: Result of Decision Variable of Construction of New lines

| From |  | To |  | Existing Line Type | Results generated by Model |  |  |  |  |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | u1 | u2 | u3 | u4 | u5 | u6 | u7 | u8 |  |
| Bus no. | Bus name | Bus no | Bus name |  |  |  |  |  |  |  |  |  |  |
| 1 | NewKhimti | 2 | Bahrabise | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | No expansion need |
| 2 | Bahrabise | 3 | Lapsephedi | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | No expansion need |
| 3 | Lapsephedi | 5 | Ratmate | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | No expansion need |
| 3 | Lapsephedi | 13 | Bhaktapur | 4 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Line type 5 (220 kV Double Circuit Line with Twin Bison Conductor is to be added |
| 4 | Lamosangu | 13 | Bhaktapur | 4 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Line type 5 (220 kV Double Circuit Line with Twin Bison Conductor is to be added |
| 5 | Ratmate | 16 | Hetauda | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | No expansion need |
| 9 | Balaju | 11 | Chapali | 4 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Line type 5 (220 kV Double Circuit Line with Twin Bison Conductor is to be added |
| 9 | Balaju | 10 | Suichatar | 1,3 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | Line type 4 (132 kV Double Circuit Line with 'Bear' Conductor is to be added |
| 11 | Chapali | 12 | Mulpani | 4 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Line type 5 (220 kV Double Circuit Line with Twin Bison Conductor is to be added |
| 12 | Mulpani | 13 | Bhaktapur | 4 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | Line type 5 (220 kV Double Circuit Line with Twin Bison Conductor is to be added |
| 10 | Suichatar | 14 | Matatirtha | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | No expansion needed |
| 14 | Matatirtha | 7 | Trisuli3B | 6 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | Line type 5 (220 kV Double Circuit Line with Twin Bison Conductor is to be added |
| 7 | Trisuli3B | 8 | Samundratar | 4 | 0 | 1 | 0 | 0 |  | 0 | 0 | 0 | No expansion needed |
| 6 | Chilime | 7 | Trisuli3B | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | No expansion needed |
| 14 | Matatirtha | 15 | Kulekhani-II | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | No expansion needed |
| 15 | Kulekhani-II | 16 | Hetauda | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | No expansion needed |
| 16 | Hetauda | 17 | Bharatpur 132 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 11 | Chapali | 21 | Chabel | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 21 | Chabel | 22 | Lainchaur | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 22 | Lainchaur | 9 | Balaju | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 9 | Balaju | 23 | TrisuliHEP | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 23 | TrisuliHEP | 24 | DevighatHEP | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 24 | DevighatHEP | 11 | Chapali | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 25 | ChilimeHEP | 23 | TrisuliHEP | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 10 | Suichatar | 19 | Patan | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 66 kV SC line needs to be added |
| 19 | Patan | 20 | Baneshwor | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 20 | Baneshwor | 13 | Bhaktapur | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 10 | Suichatar | 18 | Kulekhani-I | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| 18 | Kulekhani-I | 16 | Hetauda | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | No expansion needed |
| Total Cost of expansion (in MUSD) |  |  |  |  |  |  |  |  |  |  |  |  | 72.409 |

The result generated by the planning model shows that Lapsephedi-Bhaktapur, Lamosangu-Bhaktapur, Balaju-Chapali, Chapali-Mulpani, Mulpani-Bhaktapur lines should be further supported by additional 220 kV Double circuit lines having “Twin Bison” ACSR Conductor. Also Double-Circuit 66 kV line should be added in the   Balaju-Suichatar line corridor.

The result shows that the transmission expansion planning of Bagmati province is mostly to be done either in the transmission corridors of Kathmandu valley or the line corridors connecting the substations of Kathmandu valley because of the highest concentration of the load. Further, the most of the lines resulted in the expansion planning is 220 kV Double-circuit types with “Twin Bison” conductor. The reason for that can be interpreted as, even using this type of conductor, the line loadability will not exceed 75% of line capacity and there is no need to choose the line type having higher power transfer capability with increased cost.

The result of the power flow in the transmission system and the status of the line loadability for the expansion solution is presented in the Table 4.10.

Table 4.10: Power Flow Results for expansion Solution

| From |  | To |  | No. of Circuit | Length (km) | Voltage level (kV) | Conductor Type | Power Flow (MW) | Line Capacity (MW) | % Line Loadability |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Bus no. | Bus name | Bus no | Bus name |  |  |  |  |  |  |  |
| 1 | New-Khimti | 2 | Bahrabise | 2 | 46 | 400 | Quad moose | -269.44 | 4230.00 | 6.37% |
| 2 | Bahrabise | 3 | Lapsephedi | 2 | 60 | 400 | Quad moose | 104.38 | 4230.00 | 2.47% |
| 3 | Lapsephedi | 5 | Ratmate | 2 | 28 | 400 | Quad moose | -385.83 | 4230.00 | 9.12% |
| 3 | Lapsephedi | 13 | Bhaktapur | 2 | 14 | 132 | Bear | 103.25 | 220.00 | 46.93% |
| 3 | Lapsephedi 220 | 13 | Bhaktapur 220 | 2 | 14 | 220 | Twin Bison | 409.85 | 907.00 | 45.19% |
| 4 | Lamosangu | 13 | Bhaktapur | 2 | 48 | 132 | Bear | 118.12 | 220.00 | 53.69% |
| 4 | Lamosangu | 13 | Bhaktapur | 2 | 48 | 220 | Twin Bison | 468.87 | 907.00 | 51.69% |
| 5 | Ratmate | 16 | Hetauda | 2 | 41 | 400 | Quad moose | 769.84 | 4230.00 | 18.20% |
| 9 | Balaju | 11 | Chapali | 2 | 5.5 | 132 | Bear | -104.41 | 220.00 | 47.46% |
| 9 | Balaju 220 | 11 | Chapali 220 | 2 | 5.5 | 220 | Twin Bison | -414.41 | 907.00 | 45.69% |
| 9 | Balaju | 10 | Suichatar | 1 | 4.9 | 132 | Bear | 79.97 | 110.00 | 72.70% |
| 9 | Balaju | 10 | Suichatar | 2 | 4.9 | 132 | Bear | 143.38 | 220.00 | 65.17% |
| 9 | Balaju 66 | 10 | Suichatar 66 | 2 | 4.9 | 66 | Wolf | 54.07 | 81.20 | 66.58% |
| 11 | Chapali | 12 | Mulpani | 2 | 3.5 | 132 | Bear | -132.50 | 220.00 | 60.23% |
| 11 | Chapali 220 | 12 | Mulpani 220 | 2 | 3.5 | 220 | Twin Bison | -525.93 | 907.00 | 57.99% |
| 12 | Mulpani | 13 | Bhaktapur | 2 | 3.5 | 132 | Bear | -172.75 | 220.00 | 78.52% |
| 12 | Mulpani 220 | 13 | Bhaktapur 220 | 2 | 3.5 | 220 | Twin Bison | -685.67 | 907.00 | 75.60% |
| 10 | Suichatar | 14 | Matatirtha | 2 | 4 | 132 | Bear | -218.50 | 220.00 | 99.32% |
| 14 | Matatirtha | 7 | Trisuli3B | 2 | 42 | 220 | Twin Moose | -649.23 | 1163.00 | 55.82% |
| 14 | Matatirtha | 7 | Trisuli3B | 2 | 42 | 220 | Twin Bison | -638.18 | 907.00 | 70.36% |
| 7 | Trisuli3B | 8 | Samundratar | 2 | 52 | 132 | Bear | -216.00 | 220.00 | 98.18% |
| 6 | Chilime | 7 | Trisuli3B | 2 | 40 | 220 | Twin Bison | 822.00 | 907.00 | 90.63% |
| 14 | Matatirtha | 15 | Kulekhani-II | 2 | 36 | 132 | Bear | -11.58 | 220.00 | 5.26% |
| 15 | Kulekhani-II | 16 | Hetauda | 2 | 8 | 132 | Bear | 20.41 | 220.00 | 9.28% |
| 16 | Hetauda | 17 | Bharatpur | 1 | 73 | 132 | Bear | -47.37 | 110.00 | 43.06% |
| 11 | Chapali | 21 | Chabel | 2 | 5 | 66 | Dog | 5.73 | 40.50 | 14.15% |
| 21 | Chabel | 22 | Lainchaur | 1 | 7 | 66 | Wolf | 5.73 | 40.50 | 14.15% |
| 22 | Lainchaur | 9 | Balaju | 1 | 2 | 66 | Wolf | 5.73 | 40.50 | 14.15% |
| 9 | Balaju | 23 | TrisuliHEP | 2 | 29 | 66 | Wolf | -38.70 | 81.20 | 47.66% |
| 23 | TrisuliHEP | 24 | DevighatHEP | 1 | 4.56 | 66 | Wolf | 2.02 | 40.50 | 4.99% |
| 24 | DevighatHEP | 11 | Chapali | 1 | 29.3 | 66 | Wolf | 16.12 | 40.50 | 39.80% |
| 25 | ChilimeHEP | 23 | TrisuliHEP | 1 | 39 | 66 | Wolf | 22.00 | 40.50 | 54.32% |
| 10 | Suichatar | 19 | Patan | 2 | 6.4 | 66 | Wolf | 73.86 | 81.20 | 90.95% |
| 10 | Suichatar | 19 | Patan | 1 | 6.4 | 66 | Wolf | 36.97 | 40.50 | 91.28% |
| 19 | Patan | 20 | Baneshwor | 1 | 3.6 | 66 | LGJ 120 | -39.17 | 40.50 | 96.72% |
| 20 | Baneshwor | 13 | Bhaktapur | 1 | 10.8 | 66 | LGJ 120 | -39.17 | 40.50 | 96.72% |
| 10 | Suichatar | 18 | Kulekhani-I | 2 | 29 | 66 | Wolf | -35.47 | 81.20 | 43.68% |
| 18 | Kulekhani-I | 16 | Hetauda | 2 | 16 | 66 | Wolf | 44.52 | 81.20 | 54.83% |

In the above Table 4.10, the highlighted line segment are the additional lines to be added in the high voltage transmission system of Bagmati Province. The expansion solution generated by the model shows that addition of the eight new lines can solve the problem of the line overloading.

# CONCLUSIONS AND RECOMMENDATIONS

## Conclusions

In this thesis, the transmission system of Bagmati province of Nepal has been studied considering the load-generation scenario of the year 2040. This static Load flow analysis of the transmission system of the region for the load-generation scenario for the year 2040 suggests that out of 32 high voltage lines, 14 will be overloaded beyond their maximum power transfer capability. Mainly, Lamosangu- Bhaktapur 132 kV double circuit line, Lapsephedi- Bhaktapur 132 kV double circuit line, Balaju-Suichatar 132 kV single circuit lines, and Suichatar- Matatirtha 132 kV lines are overloaded by more than double their capacity.

To find out the optimal expansion plan for the region, an expansion planning procedure is proposed based on mixed integer linear programming. The planning model is developed to solve the Transmission Expansion Planning (TEP) problem involving different voltage levels which have not been considered in the past literatures.

The developed planning model has been implemented in the General Algebraic Modelling Language (GAMS) software. Before implementing the model for solving the realistic transmission expansion problem of Bagmati Province of Nepal, the developed model is successfully tested using the Garver 6 bus test system. The result for the expansion of modified Garver six bus system is found to be 129.86 Million USD while that reported by Alguacil et al., (2003) is 140 Million USD. This shows that the proposed model for high voltage transmission planning provides more economic solution to the netwok planner without compromizing the technical requirements.

In implementing the model to solve the transmission expansion problem of Bagmati province, the result generated by the planning model shows that Lapsephedi-Bhaktapur, Lamosangu- Bhaktapur, Balaju-Chapali, Chapali-Mulpani, and Mulpani-Bhaktapur lines should be further supported by additional 220 kV Double circuit lines having “Twin Bison” ACSR Conductors. Also, the Suichatar- Patan line corridor should be expanded with the additional Single Circuit 66 kV lines having “Wolf” conductor.  The expansion cost for the whole expansion of high voltage networks of Bagmati Province is found to be 72.409 Million USD. However, this is to be noted that the expansion cost resulted from the modeling is for the Supply of the material and construction of the lines only and it does not include the cost of various social factors including the land acquisition.

## Recommendations

While this thesis work provides an insight into a simple yet useful methodology of transmission expansion planning of a real power system taking the case of transmission system of Bagmati Province and considering the different voltage level into the expansion planning, the research work presented here has certain limitations and some of these limitations can be explored in further research works. The following further work can be proposed:

- Consideration for the system losses in the modeling: Since transmission line losses are not taken into account while modeling, a more accurate model can be formulated taking the transmission line losses in the modeling.

- Transmission expansion planning with N-1 security constraints can added in the planning model for to check the reliability of the transmission system.

- Use of power flow controller and transmission line switching are other areas that can also be explored in the future researches.

# REFERENCES

Akbari, T., & Tavakoli Bina, M. (2014). A linearized formulation of AC multi-year transmission expansion planning: A mixed-integer linear programming approach. Electric Power Systems Research, 114, 93–100. https://doi.org/10.1016/j.epsr.2014.04.013

Alguacil, N., Motto, A. L., & Conejo, A. J. (2003). Transmission expansion planning: A mixed-integer LP approach. IEEE Transactions on Power Systems, 18(3), 1070–1077. https://doi.org/10.1109/TPWRS.2003.814891

Binato, S., Pereira, M. V. F., & Granville, S. (2001). A new Benders decomposition approach to solve power transmission network design problems. IEEE Transactions on Power Systems, 16(2), 235–240. https://doi.org/10.1109/59.918292

CBS. (2021). Nepal in Figure. https://cbs.gov.np/wp-content/upLoads/2022/08/Neapl-In-Figures-2022.pdf

CEA. (2013). MANUAL ON TRANSMISSION PLANNING CRITERIA (Issue January). Central Electricity Authority. New Delhi. https://doi.org/10.1190/segam2013-0137.1

CEA. (2018). COMPENDIUM OF TESTED TOWER DESIGNS. Central Electricity Authority. New Delhi.

Chebbo, H. M. (2000). Power Transmission Planning Using Heuristic Optimisation Techniques: Deterministic Crowding Genetic Algorithms and Ant Colony Search Methods.

Correa, C. A., Bolaños, R., & Escobar, A. (2014). Transmission expansion planning considering multiple generation scenarios and demand uncertainty Planeamiento de expansión de la transmisión considerando múltiples escenarios de generación e incertidumbre en la demanda. In Ingeniare. Revista chilena de ingeniería (Vol. 22, Issue 2).

Dubey, H. M., Pandit, M., & Sharma, J. A. Y. D. E. V. (2010). Transmission Expansion Planning in Restructured Power System : an Overview. Journal of Electrical Engineering, December, 1–8.

Esmaili, M., Ghamsari-Yazdel, M., Amjady, N., & Conejo, A. J. (2020). Short-Circuit Constrained Power System Expansion Planning Considering Bundling and Voltage Levels of Lines. IEEE Transactions on Power Systems, 35(1), 584–593. https://doi.org/10.1109/TPWRS.2019.2926410

Farrag, M. A., Ali, K. M., & Omran, S. (2019). AC load flow based model for transmission expansion planning. Electric Power Systems Research, 171, 26–35. https://doi.org/10.1016/j.epsr.2019.02.006

Garcés, L. P., Conejo, A. J., García-Bertrand, R., & Romero, R. (2009). A bilevel approach to transmission expansion planning within a market environment. IEEE Transactions on Power Systems, 24(3), 1513–1522. https://doi.org/10.1109/TPWRS.2009.2021230

Garver, L. L. (1970). Network Estimation Using Linear Programming. IEEE TRANSACTIONS ON POWER APPARATUS AND SYSTEMS, PAS-89(7).

GoN. (2015). Constitution of Nepal, 2015. Government of Nepal.

Henneaux, P., Leonardo RESE, I., & Yves SMEERS, P. (2016). Optimal Transmission Expansion Planning.

Hui Zhang,  by, Vittal, V., Gerald Heydt, C.-C. T., & Hans Mittelmann Kory W Hedman, C.-C. D. (2013). Transmission Expansion Planning for Large Power Systems by the Graduate Supervisory Committee.

IDML. (2076). State of Industrial Districts. Industial District Management Limited. https://idm.org.np/present-state-of-industrial-districts

Kaur, R., Kaur, T., & Kumar, M. (2017). An analyatical approach for transmission expansion planning with generation variations. Conference Proceedings - 2017 17th IEEE International Conference on Environment and Electrical Engineering and 2017 1st IEEE Industrial and Commercial Power Systems Europe, EEEIC / I and CPS Europe 2017, 2(2). https://doi.org/10.1109/EEEIC.2017.7977849

Kazemi, M., & Ansari, M. R. (2022). An integrated transmission expansion planning and battery storage systems placement - A security and reliability perspective. International Journal of Electrical Power and Energy Systems, 134(June 2021), 107329. https://doi.org/10.1016/j.ijepes.2021.107329

Khodaei, A., Shahidehpour, M., & Kamalinia, S. (2010). Transmission switching in expansion planning. IEEE Transactions on Power Systems, 25(3), 1722–1733. https://doi.org/10.1109/TPWRS.2009.2039946

Latorre, G., Darío Cruz, R., Areiza, J. M., & Villegas, A. (2003). Classification of publications and models on transmission expansion planning. IEEE Transactions on Power Systems, 18(2), 938–946. https://doi.org/10.1109/TPWRS.2003.811168

Lumbreras, S. (2021). Transmission Expansion Planning: The Network Challenges of the Energy Transition. In Transmission Expansion Planning: The Network Challenges of the Energy Transition. https://doi.org/10.1007/978-3-030-49428-5

Mahdavi, M., Macedo, L. H., & Romero, R. (2018). Transmission and Generation Expansion Planning Considering System Reliability and Line Maintenance. 26th Iranian Conference on Electrical Engineering, ICEE 2018, 1005–1010. https://doi.org/10.1109/ICEE.2018.8472461

MOEWRI. (2018). Present Situation and Future Roadmap of Energy, Water Resources and Irrigation Sector (White Paper). Ministry of Energy, Water Resources and Irrigation. Government of Nepal.

Mutlu, S., & Şenyiğit, E. (2021). Literature review of transmission expansion planning problem test systems: detailed analysis of IEEE-24. Electric Power Systems Research, 201(September). https://doi.org/10.1016/j.epsr.2021.107543

NEA. (2022). A YEAR IN REVIEW-FISCAL YEAR 2021/2022. Nepal Electricity Authority. Nepal.

Romero, R., & Monticelli, A. (1994). A hierarchical decomposition approach for transmission network expansion planning. IEEE Transactions on Power Systems, 9(1), 373–380. https://doi.org/10.1109/59.317588

RPGCL. (2018). Transmission System Development Plan of Nepal. Rastriya Prasaran Grid Company Limited. Nepal.

Sainju, D., Sinha, R., & Pokhrel, B. R. (2016). Static expansion planning of transmission line using Mixed Integer Linear Programming method. 2016 IEEE 6th International Conference on Power Systems, ICPS 2016, 1–6. https://doi.org/10.1109/ICPES.2016.7584141

Seifi, H., Sepasian, M. S., Haghighat, H., Foroud, A. A., Yousefi, G. R., & Rae, S. (2007). Multi-voltage approach to long-term network expansion planning. IET Generation, Transmission and Distribution, 1(5), 826–835. https://doi.org/10.1049/iet-gtd:20070092

Slednev, V., Ruppert, M., Bertsch, V., Fichtner, W., Meyer-Hübner, N., Suriyah, M., Leibfried, T., Gerstner, P., Schick, M., & Heuveline, V. (2017). Regionalizing input data for generation and transmission expansion planning models. Trends in Mathematics, 190029, 205–217. https://doi.org/10.1007/978-3-319-51795-7_13

Soroudi, A. (2017). Power system optimization modeling in GAMS. In Power System Optimization Modeling in GAMS. https://doi.org/10.1007/978-3-319-62350-4

Villasana, R., York, N., & Garver, L. L. (1985). EPL ]. 2, 349–356.

Westerberg, H., Bjorklund, B., Hultman, E., & February, I. (1977). Mixed ­ Integer Linear Programming Basics.

- APPENDIX A: GENERATION DATA FOR YEAR 2040

| Hub/Substation | Hydropower | Capacity (MW) | Total |
| --- | --- | --- | --- |
| Ratmate | Budhi Gandaki Storage Hydropower Project | 1200 | 1305.67 |
|  | Trishuli Galchhi | 75 |  |
|  | Ratmate Cluster 1 | 3.67 |  |
|  | Balaju Cluster | 23.7 |  |
|  | Ratmate Cluster 2 | 3.3 |  |
| New Hetauda | Kulekhani-II | 32 | 81.04 |
|  | Kulekhani III | 14 |  |
|  | Bagmati Nadi | 22 |  |
|  | New Hetauda Cluster | 13.04 |  |
| Trishuli 3B | Upper Trishuli-1 | 216 | 476.77 |
|  | Upper Trishuli 3B | 37 |  |
|  | Upper Trishuli 3A | 60 |  |
|  | Middle Trishuli Ganga nadi | 65 |  |
|  | Trishuli | 24 |  |
|  | Trishuli 3B Cluster 1 | 25.55 |  |
|  | Trishuli 3B Cluster 2 | 49.22 |  |
| Samundratar | Samundratar Cluster | 44.69 | 69.39 |
|  | Super Melamchi Hydropower Project | 24.7 |  |
|  | Super Aankhu Khola Hydropower Project | 25.4 | 179.6 |
|  | Akhu Khola-2 HPP | 20 |  |
|  | Tatopani khola HPP | 24.3 |  |
|  | Ilep Tatopani Khola HPP | 25 |  |
|  | Upper Ankhu Khola | 35 |  |
|  | Ankhu Khola | 42.9 |  |
|  | Ankhu Khola Cluster | 7 |  |
| Chilime | Upper Trishui-2 HPP | 102 | 844.15 |
|  | Sanjen | 42.5 |  |
|  | Mathillo Langtang HEP | 24.35 |  |
|  | Chilime | 22 |  |
|  | Sanjen Khola | 78 |  |
|  | Rasuwagadhi | 111 |  |
|  | Rasuwa Bhotekoshi | 120 |  |
|  | Lantang Khola Reservoir Hydropower Project | 310 |  |
|  | Chilime Cluster 1 | 34.3 |  |
|  | Kulekhani-I | 60 | 89.71 |
| Kulekhani I | Kulekhani-I Cluster | 29.71 |  |
| Lapsephedi | Lapsephedi Cluster | 22.9 | 22.9 |
| Bahrabise | Madhya Bhotekoshi | 102 | 128.25 |
|  | Bahrabise Cluster | 26.25 |  |
| Lower Balephi hub | Upper Balephi A | 36 | 93.08 |
|  | Balephi | 23.52 |  |
|  | Balephi Cluster | 33.56 |  |
| Upper Balephi Hub | Nyasim Hydropower Project | 35 | 209.68 |
|  | Upper Balephi Cluster | 7.27 |  |
|  | Upper Brahmayeni HEP | 20.07 |  |
|  | Brahmayani HPP | 40 |  |
|  | Balephi Khola HEP | 42.14 |  |
|  | Upper Nyasim Khola | 43 |  |
|  | Upper Balefhi | 22.2 |  |
| Bhotekoshi | Upper Chaku A | 45 | 210.68 |
|  | Upper Bhotekoshi | 46 |  |
|  | Middle Bhotekoshi -1 | 40 |  |
|  | Bhotekoshi 1 Hydropower Project | 44 |  |
|  | Bhotekoshi Cluster | 35.68 |  |
| Lamosangu | Lower Balephi | 20 | 89 |
|  | Lamosangu Cluster | 9 |  |
|  | Bhotekoshi 5 | 60 |  |
| Singati | Khani Khola - 1 | 40 | 287.79 |
|  | Khare Hydropower Project | 24.1 |  |
|  | Khani Khola (Dolakha | 30 |  |
|  | Tamakoshi-V | 87 |  |
|  | Sagu Khola HEP | 20 |  |
|  | Singati Cluster 1 | 51.24 |  |
|  | Singati Cluster 2 | 35.45 |  |
| New Khimti | Tamakoshi-3 TA-3 | 650 | 1002.02 |
|  | Lower Likhu | 28.1 |  |
|  | Khimti -I | 60 |  |
|  | Khimti II | 48.8 |  |
|  | New Khimti Cluster | 15.12 |  |
|  | Khimti Shivalaya Storage HPP | 200 |  |
| Garjyang Hub | Khimti Shivalaya Cluster | 30.23 | 87.73 |
|  | Nupche Likhu HEP | 57.5 |  |
| Likhu Hub | Likhu Khola HPP | 30 | 296.92 |
|  | Likhu-4 | 52.4 |  |
|  | Likhu Khola 'A' | 51 |  |
|  | Likhu Cluster | 31.52 |  |
|  | Likhu -2 | 55 |  |
|  | Likhu -1 | 77 |  |
| Lapche | Upper Lapche Khola | 52 | 274 |
|  | Lapche Khola | 160 |  |
|  | Jum Khola Hydropower Project | 62 |  |
| Up Tamakoshi Hub | Rolwaling Khola | 22 | 566 |
|  | Rolwaling Khola HPP | 88 |  |
|  | Upper Tamakoshi HPP | 456 |  |

# APPENDIX B: EXISTING AND UNDER COSTRUCTION TRANSMISSION LINES OF BAGMATI PROVINCE

| From |  | To |  | Length (km) | Voltage level (kV) | Conductor Type | No of Circuit |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Bus no. | Bus name | Bus no | Bus name |  |  |  |  |
| 1 | NewKhimti | 2 | Bahrabise | 46 | 400 | Quad moose | 2 |
| 2 | Bahrabise | 3 | Lapsephedi | 60 | 400 | Quad moose | 2 |
| 3 | Lapsephedi | 5 | Ratmate | 28 | 400 | Quad moose | 2 |
| 3 | Lapsephedi | 18 | Bhaktapur | 14 | 132 | Bear | 2 |
| 4 | Lamosangu | 18 | Bhaktapur | 48 | 132 | Bear | 2 |
| 5 | Ratmate | 27 | Hetauda | 41 | 400 | Quad moose | 2 |
| 6 | Chilime HEP | 10 | Trisuli HEP | 39 | 66 | Wolf | 1 |
| 10 | Trisuli HEP | 11 | Devighat | 4.56 | 66 | Wolf | 1 |
| 10 | Trisuli HEP | 12 | Balaju | 58 | 66 | Dog | 2 |
| 11 | Devighat | 14 | Chapali | 26.5 | 66 | Dog | 2 |
| 14 | Chapali | 12 | Balaju | 5.5 | 132 | Bear | 2 |
| 14 | Chapali | 15 | Chabel | 5 | 66 | Dog | 2 |
| 14 | Chapali | 17 | Mulpani | 3.5 | 132 | Bear | 2 |
| 15 | Chabel | 16 | Lainchaur | 7 | 66 | XLPE cable | 1 |
| 16 | Lainchaur | 12 | Balaju | 2 | 66 | Panther | 1 |
| 12 | Balaju | 13 | Suichatar | 4.9 | 132 | Bear | 1 |
| 12 | Balaju | 13 | Suichatar | 7 | 66 | Wolf | 2 |
| 13 | Suichatar | 23 | Teku | 4.1 | 66 | Bear | 2 |
| 23 | Teku | 24 | K3 SS | 2.8 | 66 | XLPE cable | 2 |
| 17 | Mulpani | 18 | Bhaktapur | 3.5 | 132 | Bear | 2 |
| 13 | Suichatar | 20 | Patan | 6.4 | 66 | Wolf | 2 |
| 20 | Patan | 19 | Baneshwor | 2.7 | 66 | Wolf | 1 |
| 19 | Baneshwor | 18 | Bhaktapur | 10.8 | 66 | Wolf | 1 |
| 13 | Suichatar | 22 | Matatirtha | 4 | 132 | Bear | 2 |
| 13 | Suichatar | 25 | Kulekhani-I | 29 | 66 | Wolf | 2 |
| 22 | Matatirtha | 8 | Trisuli3B | 42 | 220 | Twin Moose | 2 |
| 8 | Trisuli3B | 9 | Samundratar | 52 | 132 | Bear | 2 |
| 8 | Trisuli3B | 7 | Chilime220 | 40 | 220 | Twin Bison | 2 |
| 22 | Matatirtha | 26 | Kulekhani-II | 36 | 132 | Bear | 2 |
| 26 | Kulekhani-II | 27 | Hetauda | 8 | 132 | Bear | 2 |
| 25 | Kulekhani-I | 27 | Hetauda | 16 | 66 | Wolf | 2 |
| 27 | Hetauda | 28 | Bharatpur | 73 | 132 | Twin Bison | 2 |

- APPENDIX C: ETAP LOAD FLOW MODEL OF BAGMATI PROVINCE

ETAP Transmission line model of Bagmati Province

- APPENDIX D: PROPERTIES OF ACSR CONDUCTOR

Properties of ACSR conductor ( Conforms to BS 215 : part 2/1970 )

- APPENDIX E: INFLATION ADJUSTMENT FOR LINE COST

| S.N | Line Voltage level | Cost per/km (for base year 2018/19) | **CPI for Non-food and Services in 2018/19 | **CPI for non-food and Services in 2021/22 | *Inflation Adjusted cost per km |
| --- | --- | --- | --- | --- | --- |
| 1 | 66 kV S/C Wolf | 0.15 | 129.55 | 149 | 0.17 |
| 2 | 66 kV D/C Wolf | 0.17 | 129.55 | 149 | 0.20 |
| 3 | 132 kV S/C BEAR | 0.23 | 129.55 | 149 | 0.26 |
| 4 | 132 kV D/C BEAR | 0.25 | 129.55 | 149 | 0.29 |
| 5 | 220 kV D/C Twin Bison | 0.52 | 129.55 | 149 | 0.60 |
| 6 | 220 kV D/C Twin Moose | 0.55 | 129.55 | 149 | 0.63 |
| 7 | 400 kV D/C Twin Bison | 0.77 | 129.55 | 149 | 0.89 |
| 8 | 400 kV D/C Quad Moose | 0.84 | 129.55 | 149 | 0.97 |

*Real price in current year= (CPI in current year/ CPI in base year)*Price in base year

**Source: Nepal Rastra Bank, Quaterly Economic Bulletin, 2022, Volume 56, Number 3

- APPENDIX F: GAMS CODE FOR TRANSMISSION EXPASION PLANNING

GAMS code for Transmission Expansion Planning of Bagmati Province

set i /1*25/;

set para /len,ELT/

linepara       / x,cost,cap /

Gen      Generators  / g1*g18 /

gp generators parameretes /Pmax,Pmin/

slack(i) reference bus /1/

LT linetype     /LT1*LT8/;

Set GB(i,Gen) 'connectivity index of each generating unit to each bus'

/

1.g1

2.g2

3.g3

4.g4

5.g5

6.g6

7.g7

8.g8

9.g9

10.g10

13.g11

15.g12

16.g13

17.g14

18.g15

23.g16

24.g17

25.g18

/;

alias(i,j) ;

Parameter   M;

Scalar

Sbase /  100 / ;

Table Demand(i,*) 'demands of each bus in MW'

Pd

1    2496

2    50

3    0

4    0

5    150

6    0

7    200

8    0

9    400

10   450

11   150

12   200

13   220

14   1079

15   0

16   2250

17   0

18   0

19   150

20   0

21   0

22   0

23   0

24   0

25   0

;

Table Linedata(i,j, *)

len    ELT

1 .2     46     8

2 .3     60     8

3 .5     28     8

3 .13    14     4

4 .13    48     4

5 .16    41     8

9. 10    4.9    3

9 .11    5.5    4

11.12    3.5    4

12.13    3.5    4

10.14    4      4

14.7     42     6

7 .8     52     4

6 .7     40     5

14.15    36     4

15.16    8      4

16.17    73     3

11.21    5      1

21.22    7      1

22.9     2      1

9 .23    29     2

23.24    4.56   1

24.11    29.3   1

25.23    39     1

10.19    6.4    2

19.20    3.6    1

20.13    10.8   1

10.18    29     2

18.16    16     2

;

Table gendata(gen,*)

Pmax        Pmin

g1     2226.56     0

g2     423.82      0

g3     22.9        0

g4     587         0

g5     1305.67     0

g6     822         0

g7     452.77      0

g8     279         0

g9     60.1        0

g10    82          0

g11    17.5        0

g12    32          0

g13    1367.84     0

g14    47.37       0

g15    80          0

g16    24          0

g17    14.1        0

g18    22          0

;

Table LD(LT,*)       'Characteristic values of different linetype for expansion planning'

x             cost       cap

LT1    0.00885       0.17       40.5

LT2    0.00443       0.20       81

LT3    0.002216      0.26       110

LT4    0.001236      0.29       220

LT5    0.0003114     0.60       906

LT6    0.0003061     0.63       1163

LT7    0.0001923     0.89       2115

LT8    0.0001582     0.97       4229 ;

Set conex(i,j);

conex(i,j)$(linedata(i,j,'len')) = 1;

conex(j,i)$conex(i,j)        = 1;

linedata(j,i,'len')$linedata(i,j,'len')=linedata(i,j,'len');

linedata(j,i,'ELT')$linedata(i,j,'ELT')=linedata(i,j,'ELT');

Parameter    Bij(i,j,LT);

Bij(i,j,LT)$conex(j,i)=0;

Bij(i,j,LT)$conex(j,i)= 1/(LD(LT,'x')*linedata(i,j,'len'));

M = smax((i,j,LT)$conex(i,j),Bij(i,j,LT)*3.14*2) ;

Variable OF,lineFlow(i,j,LT);

variable Pg(Gen), delta(i);

Binary Variable u(i,j,LT);

u.l(i,j,LT) = 0;

lineflow.l(i,j,LT)=0;

u.fx(i,j,LT)$(conex(i,j) and ord(LT)= linedata(j,i,'ELT') and linedata (i,j,'ELT')>0) = 1;

equation eq1,eq2,eq3,eq4,eq5,eq6,eq7;

eq1..

OF =e= 1000000*sum((i,j,LT)$conex(i,j), 0.5*LD(LT,'cost')*linedata(i,j,'len')*u(i,j,LT)$(ord(LT)<>linedata(j,i,'ELT')));

eq2(i)..

+sum(Gen$GB(i,Gen), Pg(Gen))-sum((LT,j)$conex(j,i), lineFlow(i,j,LT)) =e=Demand(i,'Pd')/Sbase ;

eq3(i,j,LT)$conex(j,i)..

lineFlow(i,j,LT) - (delta(i) - delta(j))/(linedata(i,j,'len')*LD(LT,'x')) =l=  M*(1 - u(i,j,LT));

eq4(i,j,LT)$conex(j,i)..

lineFlow(i,j,LT) - (delta(i) - delta(j))/(linedata(i,j,'len')*LD(LT,'x')) =g= -M*(1 - u(i,j,LT));

eq5(i,j,LT)$conex(j,i)..

lineFlow(i,j,LT)   =l= u(i,j,LT)*LD(LT,'Cap')/Sbase;

eq6(i,j,LT)$conex(j,i)..

lineFlow(i,j,LT)   =g= -u(i,j,LT)*LD(LT,'Cap')/Sbase;

eq7(i,j,LT)$conex(j,i)..

u(i,j,LT) =e= u(j,i,LT);

Pg.lo(Gen) = gendata(Gen,'Pmin')/Sbase;

Pg.up(Gen) = gendata(Gen,'Pmax')/Sbase;

delta.up(i)   = pi/6;

delta.lo(i)   =-pi/6;

delta.fx(slack) = 0;

lineFlow.up(i,j,LT)$conex(j,i) = 1*LD(LT,'cap')/Sbase;

lineFlow.lo(i,j,LT)$conex(j,i) =-1*LD(LT,'cap')/Sbase;

Model DCloadflow / all /;

solve DCloadflow minimizing OF using MIP;

Parameter report(i,*),pij(i,j,LT), Bm (i,j,LT);

report(i,'Gen(MW)')    = sum(Gen$GB(i,Gen), Pg.l(Gen))*sbase;

report(i,'Angle')      = delta.l(i);

report(i,'load(MW)')   = Demand(i,'Pd');

Pij(i,j,LT) = lineflow.l(i,j,LT)*sbase ;

display report,Pij, OF.l, u.l;

- APPENDIX G: ORIGINALITY REPORT